## INSTALLATION
Fill in blue cells
Need/pers./day (L) | Nb of pers. | Tavg storage (°C) | pipes diam. (mm) | Pipe material | H (m) | Pipe length (m) | P (mbar) | J (mmCE) | Tank volume (L) | Collector area (m²) | Collector inclination (°)
23 | 4 | 50 | 12.7 | Copper | 1.42 | 4 | 0.51558 | 1.2063 | 120.75 | 0.989 | 45
Those values depend on your design and material
[9 empty] | D (m) | 0.4 | See figure on the left
[9 empty] | hc (m) | 0.88
[9 empty] | h (m) | 1.66
[9 empty] | H (m) | 1.42
D (m)
h (m)
hc (m)

## collector
Orientation coefficient (information only)
South | +- 10° | +-20° | +-30° | +-40° | +-45°
1 | 0.99 | 0.98 | 0.96 | 0.94 | 0.92
Inclination coefficient (information only)
30° | 35° | 40° | 45°
0.93 | 0.94 | 0.95 | 1
n0 (glass optical efficiency) | Tmf (avg) (°C) | Te (ext) (°C) | U1 (conductivity heat loss coef.) (W/(m².K)) | U2 (convection heat loss coef.) (W/(m².K)) | G* (Solar radiation) (W/m²) | n (global efficiency) |  | Inclination (*) | Month | Solar energy (kWh/m²/day)
0.826 | 60 | 0 | 3.7 | 0.011 | 1000 | 56.44% |  | 45 | January | 3.71
Need / pers. (L) | Nb of pers. | Tst (avg storage) (°C) | Tef (cold tap water winter) (°C) | Energy consumption per day (kWh) | Global efficiency | Energy need per month (kWh) | Collector efficiency | G* (Solar radiation) (kWh/m²/mois) | Collector energy (kWh/m²) | Collector area (m²)
23 | 4 | 50 | 10 | 4.2798 | 80% | 64.1976 | 56.44% | 115.01 | 64.9116 | 0.989

## tank
Need / pers. (L) | Nb of pers. | Tst (avg. storage) (°C) | Tes (tap hot water) (°C) | Tef (tap cold water winter) (°C) | Safety coef | Tank volume (L)
23 | 4 | 50 | 45 | 10 | 1.5 | 120.75

## geometry
H (m) | T° start | Delta T Start/Return | Mfr (kg/m3) | Mfd (kg/m3) | Pressure drop (mmCE) | P (mmCE) | P (mbar)
1.42 | 80 | 20 | 971.81 | 958.4 | 13.7865 | 5.2557 | 0.51558

## losses
Total pressure drop ( J + Z ) defining ratio J/Z.
| 2 |  | 2 | FALSE |  | Concentration (%) | 2
Section | Description | Litres/Hour | Section length | Inner diameter mm | Pipe material | Inicital fluid temperature °C | Temperature loss | Masse volumique de l'eau Kg/M3 | Litres/Heure | Speed m/s | Viscosité cinématique | Re | A | B | C | Cpe | Pression dynamique | Flow | J in mmCE/m | J in mmCE | % J | % Z | Ratio J/Z | Z in mmCE/m | Z in mmCE | Total drop J + Z of the section in mmCE
1 |  | 41.538 | 4 | 12.7 | Copper | 80 | 20 | 977.7431 | 41.538 | 0.091085 | 4.2201e-07 | 2741.1119 | 4.7049 | 4.7187 | 4.7162 | 0.037055 | 0.42286 | Transitional | 1.2063 | 4.8253 | 35 | 65 | 0.53846 | 2.2403 | 8.9612 | 13.7865
2 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
3 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
4 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
5 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
6 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
7 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
8 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
9 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
10 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
11 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
12 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
13 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
14 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
15 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
16 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
17 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
18 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
19 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
20 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | Total |  |  |  | Avg | Moyenne | Moyenne | Avg | Moyenne | Moyenne |  |  |  | Moyenne | Moyenne |  | Avg | Total | Avg | Avg | Avg | Avg | Total | Total
|  | 41.538 | 4 |  |  |  | 20 | 977.7431 | 41.538 | 0.091085 | 2.11e-08 | 2741.1119 |  |  |  | 0.037055 | 0.021143 |  | 1.2063 | 4.8253 | 35 | 65 | 0.53846 | 2.2403 | 8.9612 | 13.7865
| Total per unit length pressure drop J in mmCE : |  |  |  |  | 4.8253
| Total singular pressure drop Z in mmCE : |  |  |  |  | 8.9612
| J/Z in % : |  |  |  |  | 35 / 65%
| Total pressure drop in mmCE : |  |  |  |  | 13.7865 | 1.3525
Power in Watts
Litres/hour
Values in Pascal
Values in mmCE
10
15
20
25
30
35
40
45
50
Glycol solution

## Mv
Water volumic mass against temperature
| T (°C) | p (kg/m3)
| 0 | 999.79
| 1 | 999.84
| 2 | 999.88
| 3 | 999.92
| 4 | 999.97
| 5 | 999.92
| 6 | 999.88
| 7 | 999.84
| 8 | 999.79
| 9 | 999.72
| 10 | 999.65
| 11 | 999.55
| 12 | 999.44
| 13 | 999.32
| 14 | 999.19
| 15 | 999.05
| 16 | 998.9
| 17 | 998.74
| 18 | 998.56
| 19 | 998.36
| 20 | 998.16
| 21 | 997.96
| 22 | 997.74
| 23 | 997.5
| 24 | 997.25
| 25 | 996.99
| 26 | 996.74
| 27 | 996.48
| 28 | 996.2
| 29 | 995.9
| 30 | 995.59
| 31 | 995.29
| 32 | 995.97
| 33 | 994.65
| 34 | 994.33
| 35 | 994.98
| 36 | 993.64
| 37 | 993.28
| 38 | 992.93
| 39 | 992.55
| 40 | 992.17
| 41 | 991.78
| 42 | 991.39
| 43 | 990.99
| 44 | 990.57
| 45 | 990.16
| 46 | 989.75
| 47 | 989.33
| 48 | 988.9
| 49 | 988.45
| 50 | 988.04
| 51 | 987.55
| 52 | 987.06
| 53 | 986.58
| 54 | 986.19
| 55 | 985.7
| 56 | 985.22
| 57 | 984.73
| 58 | 984.67
| 59 | 983.18
| 60 | 983.13
| 61 | 982.7
| 62 | 982.22
| 63 | 981.64
| 64 | 981.06
| 65 | 980.48
| 66 | 979.91
| 67 | 979.33
| 68 | 978.85
| 69 | 978.28
| 70 | 977.7
| 71 | 977.13
| 72 | 976.56
| 73 | 975.99
| 74 | 975.41
| 75 | 974.84
| 76 | 974.27
| 77 | 973.7
| 78 | 973.14
| 79 | 972.47
| 80 | 971.81
| 81 | 971.25
| 82 | 970.59
| 83 | 969.93
| 84 | 969.27
| 85 | 968.61
| 86 | 967.96
| 87 | 967.3
| 88 | 966.65
| 89 | 965.99
| 90 | 965.34
| 91 | 964.69
| 92 | 964.04
| 93 | 963.39
| 94 | 962.64
| 95 | 961.9
| 96 | 961.26
| 97 | 960.52
| 98 | 959.78
| 99 | 959.04
| 100 | 958.4
| 101 | 957.67